## invest
Verlustbewertung von Transformatoren
Verluste verursachen Folgekosten über die Lebensbetriebszeit des Transformators. Beim Kauf eines Transformators
sind also neben dem angebotenen Preis auch die Folgekosten zu bewerten, die sich mit höheren Verlustleistungen
auch erhöhen. Unter Berücksichtigung der Folgekosten ergeben sich neue Vergleichspreise für die einzelnen Ange-
bote. Weichen bei den später durchzuführenden Prüfungen die Verluste von den Garantiewerten ab, sind aber noch
im zulässigen Toleranzbereich (+15% bzw. +10% für die Gesamtverluste), dann sind basierend auf den ermittelten
Verlustüberschreitungen Strafzahlungen vom Preis abzuziehen. Derartige Vereinbarungen sind vertraglich festzulegen.
Zinssatz p = | 8% |  | Berechnung Barwertfaktor:
Nutzungsdauer n = | 20
Stromverrechnungspreis KA = | 0.08 |  | Barwertfaktor an = | (qn - 1 ) / qn ( q - 1 )
Tjahr = | 8760 |  | q = | 1 + (p/100)
q = | 1.08 |  | p = | Zinssatz in %
Barwertfaktor an = | 9.8181 |  | n = | Nutzungsdauer in Jahren
Typisches Beispiel für ein Verwaltungsgebäude
Leerlaufverluste
Betriebsdauer TB |  | 8760
bP0 | Bewertungsfaktor | 700.8 | bP0 = KA * TB
BPo | kapitalisiert | 6880.5577 | BP0 = KA * TB * an
Kurzschlußverluste
S/SN |  | 0.65 | Verhältnis Bedarfsleistung / Trafo-Nennleistung
Betriebsdauer TB |  | 8760
Arbeitsverlustfaktor d |  | 0.3 | d = f (Jahresbenutzerstunden/Jahresbetriebsdauer)
bPK | Bewertungsfaktor | 88.8264 | bPK = KA * d * TB * (S/SN)²
BPk | kapitalisiert | 872.1107 | BPK = KA * d * TB * (S/SN)² * an
Fuer dieses Ergebnis gilt: | pro Watt überschreiten der Leerlaufverluste |  | 6.8806 | € Strafzahlungen ansetzbar.
|  | und pro Watt überschreiten der Lastverluste koennen | 0.87211 | €. Strafzahlungen angesetzt werden.
Losses Evaluation for Transformers
Losses will cause costs during the service life of a transformer. When purchasing a transformer not only the offered
prices need to be compared between different bidders, but also the offered losses of the particular transformers. This
will lead to new virtual prices (net present values of losses added to transformer price) to be compared. In case the
quoted losses, measured during tests after purchasing, will be exceeded, but are still within the permissible tolerance
ranges (+15% resp. +10% for total losses), penalty payments can be deducted from the transformer price in the
amount of the calculated net present cash value of the losses. But such procedures need to be fixed in the contract.
interest rate i = | 8% |  | Calculation of Net Present Value factor:
service life n = | 20
power costs PkWh = | 0.08 |  | Net present value factor NPVn = | (qn - 1 ) / qn ( q - 1 )
hours per year Tyear = | 8760 |  | q = | 1 + (p/100)
q = | 1.08 |  | i = | interest rate in %
Net Present Value factor NPVn = | 9.8181 |  | n = | service life in years
Typical example for office building:
No-Load Losses
operation hours per year TB |  | 8760
bP0 | evaluation factor | 700.8 | bP0 = PkWh * TB
BPo | present cash value | 6880.5577 | BP0 = PkWh * TB * NPVn
Load losses
S/SN |  | 0.65 | Ratio: power demand / transformer's rated power
operation hours per year TB |  | 8760
demand factor d |  | 0.3 | d = f (annual demand hours / annual operation hours)
bPK | evaluation factor | 88.8264 | bPK = PkWh * d * TB * (S/SN)²
BPk | present cash value | 872.1107 | BPK = PkWh * d * TB * (S/SN)² * NPVn
This means for this example: | for each Watt exceeding the no-load losses |  | 6.8806 | € can be added to the price respec-
tively deducted from the price after tests and for each Watt exceeding the load losses
|  |  | 0.87211 | € can be added respectively deducted.

## Impedanz
Transformator
uk - Berechnung |  |  |  | OS = Oberspannung
US = Unterspannung
Dyn11/5
[5 empty] | Wicklungsstrom OS ( US ), I = | 9.0909 | A
[5 empty] | S= | 300 | kVA
[5 empty] | OS ( US ) | 11000 | V
[5 empty] | OS ( US ) | 1496 | Windungen
[5 empty] | US (innen) | 17.9 | cm
[5 empty] | US(aussen) | 23.2 | cm
[5 empty] | OS (innen) | 24.8 | cm
[5 empty] | OS(aussen) | 32.9 | cm
[5 empty] | OS-Zyl. | 0.2 | cm (dick)
[5 empty] | h= | 33 | cm
[5 empty] | f= | 50 | 1/s
| A*N = | 13600 | Ampere-Windungen
| a = | 4.15
| b = | 2.65
| c = | 0.8
| Dm = | 12
| s = | 3.0667
| Ux = | 5.1189 | %
| ux = | uk
% Ux =
7.9 x ( I x N ) x 2p x Dm x f
( Uw ) x h x 1,000,000
x s
7.9 = 2 x p x mo uo
US
US
OS
OS
Dm
h
a
c
b
zentrieren
Kern
OS
US
Kern
Kern
a + b
3
+ c
s =
Kern
Ux
Ur
Uk
Durch den geringen Wirkwiderstands-anteils ur und dem daraus resultierenden kleinen Winkel zwischen uk und ux kann man ux gleich uk setzen. Uk ist der Scheinwiderstand des Transformators in Prozentangabe.

## impedance
Transformer
ez - calculation ( impedance ) |  |  |  | HV = High-Voltage coil
LV = Low-Voltage coil
Dyn11 / 5
[5 empty] | current HV ( LV ), I = | 9.0909 | A
[5 empty] | S= | 300 | kVA
[5 empty] | HV ( LV ) | 11000 | V
[5 empty] | HV ( LV ) | 1496 | turns
[5 empty] | LV (inside) | 17.9 | cm
[5 empty] | LV(outside) | 23.2 | cm
[5 empty] | HV (inside) | 24.8 | cm
[5 empty] | HV(outside) | 32.9 | cm
[5 empty] | HV-cyl. | 0.2 | cm (thick)
[5 empty] | h= | 33 | cm
[5 empty] | f= | 50 | 1/s
| A*N = | 13600 | Ampere-turns
| a = | 4.15
| b = | 2.65
| c = | 0.8
| Dm = | 12
| s = | 3.0667
| ex = | 5.1189 | %
| ex = | ez
% ex =
7.9 x ( I x N ) x 2p x Dm x f
( Uw ) x h x 1,000,000
x s
7.9 = 2 x p x mo uo
LV
LV
HV
HV
Dm
h
a
c
b
centering
HV
LV
a + b
3
+ c
s =
core
core
core
core
ex
er
ez
due the the small angle between
ez and ex they can be considered almost equal

## Spannungsfall
Spannungsfallberechnung
Der Spannungsfall zwischen Leerlauf und einer symmetrischen Belastung jeglicher Höhe für jeden
Wirkleistungsfaktor cos j kann über die Nenn-Kurzschlußspannung und die Verluste bei Nennlast berechnet
werden. Dieser Spannungsfall wird mit uj bezeichnet und auf die Nennspannung bezogen.
Für eine Belastung a = S / SN und einen vorgegebenen Wirkleistungsfaktor cos j ergibt sich :
|  | 1 | ( a * u"j )2 | 1 | ( a * u"j )4
uj = | a * u'j + | * | + | * | + | ………. )
|  | 2 | 10 2 | 8 | 10 6
Falls ukN < 20 % beträgt,
kann der 3. Summand
vernachlässigt werden und
mit : | [5 empty] | bei uKN < 4 % kann auch
| u'j = | uRN * cos j + uXN * sin j |  |  |  | der 2. Summand vernach-
lässigt werden.
und:
| u"j = | uRN * sin j - uXN * cos j
Die an den Abgangsklemmen anstehende Spannung auf der Sekundärseite des belasteten Transformator
ergibt sich zu:
|  | Ua = | UN ( 1 - uj / 100% )
Die Kurzschluss-Impedanz oder Kurzschluss-Spannung begrenzt den Kurzschluss-Strom auf :
|  | Ik = | ( IN / uk ) * 100%
Der sogenannte Dauer-Kurzschluss-Wechselstrom ist verantwortlich für die Erwärmung.
Den sogenannten dynamischen Stoss-Strom erhält durch Multiplikation dieses Stromes mit Wurzel 2 (1,41 Spitze)
und mit dem Faktor k ( üblich 1,8 ), der vom Verhältnis X / R abhängig ist.
Gelbe Zellen ausfüllen
| cos j = | 0.87 | Betrieb |  | Nennstrom IN = | 1000.0293 | A
| Lastverluste PkN = | 5 | kW |  | Kurzschluss-Wechselstrom I"k = | 20.0006 | kA
| Kurzschluss-Spannung ukN = | 5 | % |  | Stoss-Strom Is = | 50.9132 | kA
| Nennleistung SN = | 750 | kVA | Kurzschlusskräfte: F = 0.2 * I2 * l/d [ I in kA, F in N ]
| Aktuelle Belastung Sa = | 700 | kVA | ( l / d = Abstand d paralleler Sammelschienen über Länge l )
| Leerlaufspannung UN = | 433 | V
| Leerlauf-Verluste Po = | 1 | kW |  | Ua = | 420.4828 | V
| a = | 0.93333 |  |  | absoluter Spannungsfall Ud = | 12.5172 | V
| sin j = | 0.49305 |  |  | prozentualer Spannungsfall = | 2.891%
| uj = | 2.8908
| u'j = | 3.0232 | Wirkungsgrad h : | h = 100 % - |  | * 100 %
| u"j = | -3.9825
| uRN = | 0.66667 | %
| uXN = | 4.9554 | % | h = | 99.12%
uRN = | ( PkN / SN ) * 100 % |  | uXN = | ( u2kN - u2RN )0.5
Copying of this document and giving it to others and the use or communication of the contents thereof,
are forbidden without our express authority. Offenders are liable to the payment of damages.
All rights are reserved in the event of the grant of a patent or the registration of a utility model or design.
Po + a2 * Pk
a * SN * cos j + Po

## voltage drop
Voltage Regulation / Voltage drop
The voltage variation between no-load and a symmetrical load of any magnitude for any power factor can be
calculated from the rated impedance voltage and the impedance losses at rated load. It is called uj and
referred to the rated voltage. |  |  | Instead of ez in the following uk will be used !
For a given partial load a = S / SN and a given power factor cos j ,
|  | 1 | ( a * u"j )2 | 1 | ( a * u"j )4
uj = | a * u'j + | * | + | * | + | ………. )
|  | 2 | 10 2 | 8 | 10 6
If ukN < 20%, the third
summand can be disregarded
the second may also be
where: | [5 empty] | disregarded if ukN < 4 %
| u'j = | uRN * cos j + uXN * sin j
and:
| u"j = | uRN * sin j - uXN * cos j
The actual voltage at the terminals on the output side / secondary side of the loaded transformer will then be:
|  | Ua = | UN ( 1 - uj / 100% )
The short circuit impedance or impedance voltage limits the short circuit current:
|  | Ik = | ( IN / uk ) * 100%
This socalled sustained short circuit current is responsible for the thermal stress.
The short circuit current for the initial and highest dynamical stress is the above multiplied with square-root 2
( 1.41 for peak ) and the factor kappa ( usually 1.8 ), which represents the ratio X/R of the transformer.
Fill only yellow cells:
| cos j = | 0.87 |  |  | Rated Current IN = | 1000.0293 | A
| Impedance losses PkN = | 5 | kW ( load loss ) |  | Max.sustain.short circuit current I"k = | 20.0006 | kA
| Impedance voltage ukN = | 5 | % |  | Max Peak Short circuit current Is = | 50.9132 | kA
| Rated Power SN = | 750 | kVA | short circuit force: F = 0.2 * I2 * l/d [ I in kA, F in N ]
| Actual Load/Power Sa = | 700 | kVA | ( l/d = ratio of parallel run of busbars over distance of busbars )
| No-Load-voltage UN = | 433 | V
| No-Load-Losses Po = | 1 | kW |  | Ua = | 420.4828 | V
| a = | 0.93333 |  |  | voltage drop Ud = | 12.5172 | V
| sin j = | 0.49305 |  |  | voltage drop = | 2.891%
| uj = | 2.8908
| u'j = | 3.0232 | Efficiency h : | h = 100 % - |  | * 100 %
| u"j = | -3.9825
| uRN = | 0.66667 | %
| uXN = | 4.9554 | % | h = | 99.12%
Copying of this document and giving it to others and the use or communication of the contents thereof,
are forbidden without our express authority. Offenders are liable to the payment of damages.
All rights are reserved in the event of the grant of a patent or the registration of a utility model or design.
Po + a2 * Pk
a * SN * cos j + Po

## Hauptdaten main data
Ermittlung der Hauptdaten / Calculation of main data
20,5 * U1
N1 =
w * B * A * 0,0001 m2/cm2
Beispiel / example:
z.B./ e.g. | 909 | N1 = | 909.4104 | turns / Windungen
primaer / primary
z.B./ e.g. | 36 | N2 = | 36.3764 | turns / Windungen |  | Dd
sekundaer / secondary
z.B./ e.g. | 21 | N2 = | 21.0019 | turns / Windungen |  | Dy
sekundaer / secondary
z.B./ e.g. | 10000 | U1 = | 10000 | Volts | primaer / primary
z.B./ e.g. | 1.65 | B = | 1.65 | Tesla (Induktion/Induction)
z.B./ e.g. | 300 | A = | 300 | cm2 (Kernquerschnitt/core-cross-section)
z.B./ e.g. | 50 | f = | 50 | 1/s, Hz (Frequenz/frequency)
z.B./ e.g. | 400 | U2 = | 400 | Volts | sekundaer / secondary
|  | 20,5 = | 1.4142
|  |  | 0.0001 | m2 / cm2
|  | w = | 314.1593
U1
U2
U1
U2
Dd
Dy